## line
P	N			Armour	Sheath	D			item_name	item_category	designation	conductor_material	insulation_material	conductor_cross_section	neutral_xsec	type_of_cable	x_ohm_per_km	c_nf_per_km	armour_material	armour_cross_section
1.5	1.5	2x1.5 Y							2x1.5 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	2x1.5 Y	Copper	PVC	1.5	1	1ph	0.17		Steel
2.5	2.5	2x2.5 Y							2x2.5 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	2x2.5 Y	Copper	PVC	2.5	1	1ph	0.17		Steel
4	4	2x4 Y							2x4 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	2x4 Y	Copper	PVC	4	1	1ph	0.17		Steel
6	6	2x6 Y							2x6 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	2x6 Y	Copper	PVC	6	1	1ph	0.17		Steel
10	10	2x10 Y							2x10 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	2x10 Y	Copper	PVC	10	1	1ph	0.17		Steel
16	16	2x16 Y							2x16 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	2x16 Y	Copper	PVC	16	1	1ph	0.17		Steel
25	25	2x25 Y							2x25 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	2x25 Y	Copper	PVC	25	1	1ph	0.17		Steel
1.5	1.5	4x1.5 Y							4x1.5 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	4x1.5 Y	Copper	PVC	1.5	1	3ph	0.17		Steel
2.5	2.5	4x2.5 Y							4x2.5 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	4x2.5 Y	Copper	PVC	2.5	1	3ph	0.17		Steel
4	4	4x4 Y							4x4 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	4x4 Y	Copper	PVC	4	1	3ph	0.17		Steel
6	6	4x6 Y							4x6 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	4x6 Y	Copper	PVC	6	1	3ph	0.17		Steel
10	10	4x10 Y							4x10 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	4x10 Y	Copper	PVC	10	1	3ph	0.17		Steel
16	16	4x16 Y							4x16 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	4x16 Y	Copper	PVC	16	1	3ph	0.17		Steel
25	25	4x25 Y							4x25 Y	PVC Insulated Copper Condutor, Single Core Cable in Conduit	4x25 Y	Copper	PVC	25	1	3ph	0.17		Steel
4	4	2x4 2XY							2x4 2XY	Copper XLPE Cables	2x4 2XY	Copper	XLPE/EPR	4	1	1ph	0.08	110	Steel
6	6	2x6 2XY							2x6 2XY	Copper XLPE Cables	2x6 2XY	Copper	XLPE/EPR	6	1	1ph	0.08	130	Steel
10	10	2x10 2XY							2x10 2XY	Copper XLPE Cables	2x10 2XY	Copper	XLPE/EPR	10	1	1ph	0.08	160	Steel
16	16	2x16 2XY							2x16 2XY	Copper XLPE Cables	2x16 2XY	Copper	XLPE/EPR	16	1	1ph	0.08	180	Steel
25	25	2x25 2XY							2x25 2XY	Copper XLPE Cables	2x25 2XY	Copper	XLPE/EPR	25	1	1ph	0.08	200	Steel
35	35	2x35 2XY							2x35 2XY	Copper XLPE Cables	2x35 2XY	Copper	XLPE/EPR	35	1	1ph	0.08	230	Steel
50	50	2x50 2XY							2x50 2XY	Copper XLPE Cables	2x50 2XY	Copper	XLPE/EPR	50	1	1ph	0.08	240	Steel
70	70	2x70 2XY							2x70 2XY	Copper XLPE Cables	2x70 2XY	Copper	XLPE/EPR	70	1	1ph	0.08	260	Steel
95	95	2x95 2XY							2x95 2XY	Copper XLPE Cables	2x95 2XY	Copper	XLPE/EPR	95	1	1ph	0.08	290	Steel
120	120	2x120 2XY							2x120 2XY	Copper XLPE Cables	2x120 2XY	Copper	XLPE/EPR	120	1	1ph	0.08	290	Steel
150	150	2x150 2XY							2x150 2XY	Copper XLPE Cables	2x150 2XY	Copper	XLPE/EPR	150	1	1ph	0.08	290	Steel
185	185	2x185 2XY							2x185 2XY	Copper XLPE Cables	2x185 2XY	Copper	XLPE/EPR	185	1	1ph	0.08	290	Steel
240	240	2x240 2XY							2x240 2XY	Copper XLPE Cables	2x240 2XY	Copper	XLPE/EPR	240	1	1ph	0.08	310	Steel
300	300	2x300 2XY							2x300 2XY	Copper XLPE Cables	2x300 2XY	Copper	XLPE/EPR	300	1	1ph	0.08	330	Steel
4		3x4 2XY							3x4 2XY	Copper XLPE Cables	3x4 2XY	Copper	XLPE/EPR	4	0	3ph	0.08	110	Steel
6		3x6 2XY							3x6 2XY	Copper XLPE Cables	3x6 2XY	Copper	XLPE/EPR	6	0	3ph	0.08	130	Steel
10		3x10 2XY							3x10 2XY	Copper XLPE Cables	3x10 2XY	Copper	XLPE/EPR	10	0	3ph	0.08	160	Steel
16		3x16 2XY							3x16 2XY	Copper XLPE Cables	3x16 2XY	Copper	XLPE/EPR	16	0	3ph	0.08	180	Steel
25		3x25 2XY							3x25 2XY	Copper XLPE Cables	3x25 2XY	Copper	XLPE/EPR	25	0	3ph	0.08	200	Steel
35		3x35 2XY							3x35 2XY	Copper XLPE Cables	3x35 2XY	Copper	XLPE/EPR	35	0	3ph	0.08	230	Steel
50		3x50 2XY							3x50 2XY	Copper XLPE Cables	3x50 2XY	Copper	XLPE/EPR	50	0	3ph	0.08	240	Steel
70		3x70 2XY							3x70 2XY	Copper XLPE Cables	3x70 2XY	Copper	XLPE/EPR	70	0	3ph	0.08	260	Steel
95		3x95 2XY							3x95 2XY	Copper XLPE Cables	3x95 2XY	Copper	XLPE/EPR	95	0	3ph	0.08	290	Steel
120		3x120 2XY							3x120 2XY	Copper XLPE Cables	3x120 2XY	Copper	XLPE/EPR	120	0	3ph	0.08	290	Steel
150		3x150 2XY							3x150 2XY	Copper XLPE Cables	3x150 2XY	Copper	XLPE/EPR	150	0	3ph	0.08	290	Steel
185		3x185 2XY							3x185 2XY	Copper XLPE Cables	3x185 2XY	Copper	XLPE/EPR	185	0	3ph	0.08	290	Steel
240		3x240 2XY							3x240 2XY	Copper XLPE Cables	3x240 2XY	Copper	XLPE/EPR	240	0	3ph	0.08	310	Steel
300		3x300 2XY							3x300 2XY	Copper XLPE Cables	3x300 2XY	Copper	XLPE/EPR	300	0	3ph	0.08	330	Steel
25	16	3.5x25 2XY							3.5x25 2XY	Copper XLPE Cables	3.5x25 2XY	Copper	XLPE/EPR	25	0.64	3ph	0.08	200	Steel
35	16	3.5x35 2XY							3.5x35 2XY	Copper XLPE Cables	3.5x35 2XY	Copper	XLPE/EPR	35	0.457	3ph	0.08	230	Steel
50	25	3.5x50 2XY							3.5x50 2XY	Copper XLPE Cables	3.5x50 2XY	Copper	XLPE/EPR	50	0.5	3ph	0.08	240	Steel
70	35	3.5x70 2XY							3.5x70 2XY	Copper XLPE Cables	3.5x70 2XY	Copper	XLPE/EPR	70	0.5	3ph	0.08	260	Steel
95	50	3.5x95 2XY							3.5x95 2XY	Copper XLPE Cables	3.5x95 2XY	Copper	XLPE/EPR	95	0.526	3ph	0.08	290	Steel
120	70	3.5x120 2XY							3.5x120 2XY	Copper XLPE Cables	3.5x120 2XY	Copper	XLPE/EPR	120	0.583	3ph	0.08	290	Steel
150	70	3.5x150 2XY							3.5x150 2XY	Copper XLPE Cables	3.5x150 2XY	Copper	XLPE/EPR	150	0.467	3ph	0.08	290	Steel
185	95	3.5x185 2XY							3.5x185 2XY	Copper XLPE Cables	3.5x185 2XY	Copper	XLPE/EPR	185	0.514	3ph	0.08	290	Steel
240	120	3.5x240 2XY							3.5x240 2XY	Copper XLPE Cables	3.5x240 2XY	Copper	XLPE/EPR	240	0.5	3ph	0.08	310	Steel
300	150	3.5x300 2XY							3.5x300 2XY	Copper XLPE Cables	3.5x300 2XY	Copper	XLPE/EPR	300	0.5	3ph	0.08	330	Steel
4	4	4x4 2XY							4x4 2XY	Copper XLPE Cables	4x4 2XY	Copper	XLPE/EPR	4	1	3ph	0.08	110	Steel
6	6	4x6 2XY							4x6 2XY	Copper XLPE Cables	4x6 2XY	Copper	XLPE/EPR	6	1	3ph	0.08	130	Steel
10	10	4x10 2XY							4x10 2XY	Copper XLPE Cables	4x10 2XY	Copper	XLPE/EPR	10	1	3ph	0.08	160	Steel
16	16	4x16 2XY							4x16 2XY	Copper XLPE Cables	4x16 2XY	Copper	XLPE/EPR	16	1	3ph	0.08	180	Steel
25	25	4x25 2XY							4x25 2XY	Copper XLPE Cables	4x25 2XY	Copper	XLPE/EPR	25	1	3ph	0.08	200	Steel
35	35	4x35 2XY							4x35 2XY	Copper XLPE Cables	4x35 2XY	Copper	XLPE/EPR	35	1	3ph	0.08	230	Steel
50	50	4x50 2XY							4x50 2XY	Copper XLPE Cables	4x50 2XY	Copper	XLPE/EPR	50	1	3ph	0.08	240	Steel
70	70	4x70 2XY							4x70 2XY	Copper XLPE Cables	4x70 2XY	Copper	XLPE/EPR	70	1	3ph	0.08	260	Steel
95	95	4x95 2XY							4x95 2XY	Copper XLPE Cables	4x95 2XY	Copper	XLPE/EPR	95	1	3ph	0.08	290	Steel
120	120	4x120 2XY							4x120 2XY	Copper XLPE Cables	4x120 2XY	Copper	XLPE/EPR	120	1	3ph	0.08	290	Steel
150	150	4x150 2XY							4x150 2XY	Copper XLPE Cables	4x150 2XY	Copper	XLPE/EPR	150	1	3ph	0.08	290	Steel
185	185	4x185 2XY							4x185 2XY	Copper XLPE Cables	4x185 2XY	Copper	XLPE/EPR	185	1	3ph	0.08	290	Steel
240	240	4x240 2XY							4x240 2XY	Copper XLPE Cables	4x240 2XY	Copper	XLPE/EPR	240	1	3ph	0.08	310	Steel
300	300	4x300 2XY							4x300 2XY	Copper XLPE Cables	4x300 2XY	Copper	XLPE/EPR	300	1	3ph	0.08	330	Steel
4	4	2x4 A2XY							2x4 A2XY	Aluminium XLPE Cables	2x4 A2XY	Aluminium	XLPE/EPR	4	1	1ph	0.08	110	Steel
6	6	2x6 A2XY							2x6 A2XY	Aluminium XLPE Cables	2x6 A2XY	Aluminium	XLPE/EPR	6	1	1ph	0.08	130	Steel
10	10	2x10 A2XY							2x10 A2XY	Aluminium XLPE Cables	2x10 A2XY	Aluminium	XLPE/EPR	10	1	1ph	0.08	160	Steel
16	16	2x16 A2XY							2x16 A2XY	Aluminium XLPE Cables	2x16 A2XY	Aluminium	XLPE/EPR	16	1	1ph	0.08	180	Steel
25	25	2x25 A2XY							2x25 A2XY	Aluminium XLPE Cables	2x25 A2XY	Aluminium	XLPE/EPR	25	1	1ph	0.08	200	Steel
35	35	2x35 A2XY							2x35 A2XY	Aluminium XLPE Cables	2x35 A2XY	Aluminium	XLPE/EPR	35	1	1ph	0.08	230	Steel
50	50	2x50 A2XY							2x50 A2XY	Aluminium XLPE Cables	2x50 A2XY	Aluminium	XLPE/EPR	50	1	1ph	0.08	240	Steel
70	70	2x70 A2XY							2x70 A2XY	Aluminium XLPE Cables	2x70 A2XY	Aluminium	XLPE/EPR	70	1	1ph	0.08	260	Steel
95	95	2x95 A2XY							2x95 A2XY	Aluminium XLPE Cables	2x95 A2XY	Aluminium	XLPE/EPR	95	1	1ph	0.08	290	Steel
120	120	2x120 A2XY							2x120 A2XY	Aluminium XLPE Cables	2x120 A2XY	Aluminium	XLPE/EPR	120	1	1ph	0.08	290	Steel
150	150	2x150 A2XY							2x150 A2XY	Aluminium XLPE Cables	2x150 A2XY	Aluminium	XLPE/EPR	150	1	1ph	0.08	290	Steel
185	185	2x185 A2XY							2x185 A2XY	Aluminium XLPE Cables	2x185 A2XY	Aluminium	XLPE/EPR	185	1	1ph	0.08	290	Steel
240	240	2x240 A2XY							2x240 A2XY	Aluminium XLPE Cables	2x240 A2XY	Aluminium	XLPE/EPR	240	1	1ph	0.08	310	Steel
300	300	2x300 A2XY							2x300 A2XY	Aluminium XLPE Cables	2x300 A2XY	Aluminium	XLPE/EPR	300	1	1ph	0.08	330	Steel
4		3x4 A2XY							3x4 A2XY	Aluminium XLPE Cables	3x4 A2XY	Aluminium	XLPE/EPR	4	0	3ph	0.08	110	Steel
6		3x6 A2XY							3x6 A2XY	Aluminium XLPE Cables	3x6 A2XY	Aluminium	XLPE/EPR	6	0	3ph	0.08	130	Steel
10		3x10 A2XY							3x10 A2XY	Aluminium XLPE Cables	3x10 A2XY	Aluminium	XLPE/EPR	10	0	3ph	0.08	160	Steel
16		3x16 A2XY							3x16 A2XY	Aluminium XLPE Cables	3x16 A2XY	Aluminium	XLPE/EPR	16	0	3ph	0.08	180	Steel
25		3x25 A2XY							3x25 A2XY	Aluminium XLPE Cables	3x25 A2XY	Aluminium	XLPE/EPR	25	0	3ph	0.08	200	Steel
35		3x35 A2XY							3x35 A2XY	Aluminium XLPE Cables	3x35 A2XY	Aluminium	XLPE/EPR	35	0	3ph	0.08	230	Steel
50		3x50 A2XY							3x50 A2XY	Aluminium XLPE Cables	3x50 A2XY	Aluminium	XLPE/EPR	50	0	3ph	0.08	240	Steel
70		3x70 A2XY							3x70 A2XY	Aluminium XLPE Cables	3x70 A2XY	Aluminium	XLPE/EPR	70	0	3ph	0.08	260	Steel
95		3x95 A2XY							3x95 A2XY	Aluminium XLPE Cables	3x95 A2XY	Aluminium	XLPE/EPR	95	0	3ph	0.08	290	Steel
120		3x120 A2XY							3x120 A2XY	Aluminium XLPE Cables	3x120 A2XY	Aluminium	XLPE/EPR	120	0	3ph	0.08	290	Steel
150		3x150 A2XY							3x150 A2XY	Aluminium XLPE Cables	3x150 A2XY	Aluminium	XLPE/EPR	150	0	3ph	0.08	290	Steel
185		3x185 A2XY							3x185 A2XY	Aluminium XLPE Cables	3x185 A2XY	Aluminium	XLPE/EPR	185	0	3ph	0.08	290	Steel
240		3x240 A2XY							3x240 A2XY	Aluminium XLPE Cables	3x240 A2XY	Aluminium	XLPE/EPR	240	0	3ph	0.08	310	Steel
300		3x300 A2XY							3x300 A2XY	Aluminium XLPE Cables	3x300 A2XY	Aluminium	XLPE/EPR	300	0	3ph	0.08	330	Steel
25	16	3.5x25 A2XY							3.5x25 A2XY	Aluminium XLPE Cables	3.5x25 A2XY	Aluminium	XLPE/EPR	25	0.64	3ph	0.08	200	Steel
35	16	3.5x35 A2XY							3.5x35 A2XY	Aluminium XLPE Cables	3.5x35 A2XY	Aluminium	XLPE/EPR	35	0.457	3ph	0.08	230	Steel
50	25	3.5x50 A2XY							3.5x50 A2XY	Aluminium XLPE Cables	3.5x50 A2XY	Aluminium	XLPE/EPR	50	0.5	3ph	0.08	240	Steel
70	35	3.5x70 A2XY							3.5x70 A2XY	Aluminium XLPE Cables	3.5x70 A2XY	Aluminium	XLPE/EPR	70	0.5	3ph	0.08	260	Steel
95	50	3.5x95 A2XY							3.5x95 A2XY	Aluminium XLPE Cables	3.5x95 A2XY	Aluminium	XLPE/EPR	95	0.526	3ph	0.08	290	Steel
120	70	3.5x120 A2XY							3.5x120 A2XY	Aluminium XLPE Cables	3.5x120 A2XY	Aluminium	XLPE/EPR	120	0.583	3ph	0.08	290	Steel
150	70	3.5x150 A2XY							3.5x150 A2XY	Aluminium XLPE Cables	3.5x150 A2XY	Aluminium	XLPE/EPR	150	0.467	3ph	0.08	290	Steel
185	95	3.5x185 A2XY							3.5x185 A2XY	Aluminium XLPE Cables	3.5x185 A2XY	Aluminium	XLPE/EPR	185	0.514	3ph	0.08	290	Steel
240	120	3.5x240 A2XY							3.5x240 A2XY	Aluminium XLPE Cables	3.5x240 A2XY	Aluminium	XLPE/EPR	240	0.5	3ph	0.08	310	Steel
300	150	3.5x300 A2XY							3.5x300 A2XY	Aluminium XLPE Cables	3.5x300 A2XY	Aluminium	XLPE/EPR	300	0.5	3ph	0.08	330	Steel
4	4	4x4 A2XY							4x4 A2XY	Aluminium XLPE Cables	4x4 A2XY	Aluminium	XLPE/EPR	4	1	3ph	0.08	110	Steel
6	6	4x6 A2XY							4x6 A2XY	Aluminium XLPE Cables	4x6 A2XY	Aluminium	XLPE/EPR	6	1	3ph	0.08	130	Steel
10	10	4x10 A2XY							4x10 A2XY	Aluminium XLPE Cables	4x10 A2XY	Aluminium	XLPE/EPR	10	1	3ph	0.08	160	Steel
16	16	4x16 A2XY							4x16 A2XY	Aluminium XLPE Cables	4x16 A2XY	Aluminium	XLPE/EPR	16	1	3ph	0.08	180	Steel
25	25	4x25 A2XY							4x25 A2XY	Aluminium XLPE Cables	4x25 A2XY	Aluminium	XLPE/EPR	25	1	3ph	0.08	200	Steel
35	35	4x35 A2XY							4x35 A2XY	Aluminium XLPE Cables	4x35 A2XY	Aluminium	XLPE/EPR	35	1	3ph	0.08	230	Steel
50	50	4x50 A2XY							4x50 A2XY	Aluminium XLPE Cables	4x50 A2XY	Aluminium	XLPE/EPR	50	1	3ph	0.08	240	Steel
70	70	4x70 A2XY							4x70 A2XY	Aluminium XLPE Cables	4x70 A2XY	Aluminium	XLPE/EPR	70	1	3ph	0.08	260	Steel
95	95	4x95 A2XY							4x95 A2XY	Aluminium XLPE Cables	4x95 A2XY	Aluminium	XLPE/EPR	95	1	3ph	0.08	290	Steel
120	120	4x120 A2XY							4x120 A2XY	Aluminium XLPE Cables	4x120 A2XY	Aluminium	XLPE/EPR	120	1	3ph	0.08	290	Steel
150	150	4x150 A2XY							4x150 A2XY	Aluminium XLPE Cables	4x150 A2XY	Aluminium	XLPE/EPR	150	1	3ph	0.08	290	Steel
185	185	4x185 A2XY							4x185 A2XY	Aluminium XLPE Cables	4x185 A2XY	Aluminium	XLPE/EPR	185	1	3ph	0.08	290	Steel
240	240	4x240 A2XY							4x240 A2XY	Aluminium XLPE Cables	4x240 A2XY	Aluminium	XLPE/EPR	240	1	3ph	0.08	310	Steel
300	300	4x300 A2XY							4x300 A2XY	Aluminium XLPE Cables	4x300 A2XY	Aluminium	XLPE/EPR	300	1	3ph	0.08	330	Steel
1.5	1.5	2x1.5 2XWY		1.4	1.24	14	10.12	0.785	2x1.5 2XWY	Copper XLPE Cables - Wire Armoured	2x1.5 2XWY	Copper	XLPE/EPR	1.5	1	1ph	0.1	90	Steel	35
2.5	2.5	2x2.5 2XWY		1.4	1.24	14	10.12	0.785	2x2.5 2XWY	Copper XLPE Cables - Wire Armoured	2x2.5 2XWY	Copper	XLPE/EPR	2.5	1	1ph	0.1	90	Steel	35
4	4	2x4 2XWY		1.4	1.24	18	14.12	0.785	2x4 2XWY	Copper XLPE Cables - Wire Armoured	2x4 2XWY	Copper	XLPE/EPR	4	1	1ph	0.08	110	Steel	49
6	6	2x6 2XWY		1.4	1.24	19	15.12	0.785	2x6 2XWY	Copper XLPE Cables - Wire Armoured	2x6 2XWY	Copper	XLPE/EPR	6	1	1ph	0.08	130	Steel	52
10	10	2x10 2XWY		1.4	1.24	20	16.12	0.785	2x10 2XWY	Copper XLPE Cables - Wire Armoured	2x10 2XWY	Copper	XLPE/EPR	10	1	1ph	0.08	160	Steel	56
16	16	2x16 2XWY		1.4	1.4	19	14.8	0.785	2x16 2XWY	Copper XLPE Cables - Wire Armoured	2x16 2XWY	Copper	XLPE/EPR	16	1	1ph	0.08	180	Steel	51
25	25	2x25 2XWY		1.6	1.4	21	16.6	0.785	2x25 2XWY	Copper XLPE Cables - Wire Armoured	2x25 2XWY	Copper	XLPE/EPR	25	1	1ph	0.08	200	Steel	65
35	35	2x35 2XWY		1.6	1.4	23	18.6	0.785	2x35 2XWY	Copper XLPE Cables - Wire Armoured	2x35 2XWY	Copper	XLPE/EPR	35	1	1ph	0.08	230	Steel	73
50	50	2x50 2XWY		1.6	1.4	25	20.6	0.785	2x50 2XWY	Copper XLPE Cables - Wire Armoured	2x50 2XWY	Copper	XLPE/EPR	50	1	1ph	0.08	240	Steel	81
70	70	2x70 2XWY		1.6	1.56	28	23.28	0.785	2x70 2XWY	Copper XLPE Cables - Wire Armoured	2x70 2XWY	Copper	XLPE/EPR	70	1	1ph	0.08	260	Steel	92
95	95	2x95 2XWY		2	1.56	31	25.88	0.785	2x95 2XWY	Copper XLPE Cables - Wire Armoured	2x95 2XWY	Copper	XLPE/EPR	95	1	1ph	0.08	290	Steel	128
120	120	2x120 2XWY		2	1.56	34	28.88	0.785	2x120 2XWY	Copper XLPE Cables - Wire Armoured	2x120 2XWY	Copper	XLPE/EPR	120	1	1ph	0.08	290	Steel	142
150	150	2x150 2XWY		2	1.72	37	31.56	0.785	2x150 2XWY	Copper XLPE Cables - Wire Armoured	2x150 2XWY	Copper	XLPE/EPR	150	1	1ph	0.08	290	Steel	156
185	185	2x185 2XWY		2	1.88	40	34.24	0.785	2x185 2XWY	Copper XLPE Cables - Wire Armoured	2x185 2XWY	Copper	XLPE/EPR	185	1	1ph	0.08	290	Steel	169
240	240	2x240 2XWY		2.5	2.04	45	38.42	0.785	2x240 2XWY	Copper XLPE Cables - Wire Armoured	2x240 2XWY	Copper	XLPE/EPR	240	1	1ph	0.08	310	Steel	237
300	300	2x300 2XWY		2.5	2.2	49	42.1	0.785	2x300 2XWY	Copper XLPE Cables - Wire Armoured	2x300 2XWY	Copper	XLPE/EPR	300	1	1ph	0.08	330	Steel	259
1.5		3x1.5 2XWY		1.4	1.24	52	48.12	0.785	3x1.5 2XWY	Copper XLPE Cables - Wire Armoured	3x1.5 2XWY	Copper	XLPE/EPR	1.5	0	3ph	0.1	90	Steel	166
2.5		3x2.5 2XWY		1.4	1.24	60	56.12	0.785	3x2.5 2XWY	Copper XLPE Cables - Wire Armoured	3x2.5 2XWY	Copper	XLPE/EPR	2.5	0	3ph	0.1	90	Steel	194
4		3x4 2XWY		1.4	1.4	66	61.8	0.785	3x4 2XWY	Copper XLPE Cables - Wire Armoured	3x4 2XWY	Copper	XLPE/EPR	4	0	3ph	0.08	110	Steel	213
6		3x6 2XWY		1.4	1.4	19	14.8	0.785	3x6 2XWY	Copper XLPE Cables - Wire Armoured	3x6 2XWY	Copper	XLPE/EPR	6	0	3ph	0.08	130	Steel	51
10		3x10 2XWY		1.4	1.4	21	16.8	0.785	3x10 2XWY	Copper XLPE Cables - Wire Armoured	3x10 2XWY	Copper	XLPE/EPR	10	0	3ph	0.08	160	Steel	58
16		3x16 2XWY		1.6	1.4	20	15.6	0.785	3x16 2XWY	Copper XLPE Cables - Wire Armoured	3x16 2XWY	Copper	XLPE/EPR	16	0	3ph	0.08	180	Steel	62
25		3x25 2XWY		1.6	1.4	23	18.6	0.785	3x25 2XWY	Copper XLPE Cables - Wire Armoured	3x25 2XWY	Copper	XLPE/EPR	25	0	3ph	0.08	200	Steel	73
35		3x35 2XWY		1.6	1.4	25	20.6	0.785	3x35 2XWY	Copper XLPE Cables - Wire Armoured	3x35 2XWY	Copper	XLPE/EPR	35	0	3ph	0.08	230	Steel	81
50		3x50 2XWY		1.6	1.56	29	24.28	0.785	3x50 2XWY	Copper XLPE Cables - Wire Armoured	3x50 2XWY	Copper	XLPE/EPR	50	0	3ph	0.08	240	Steel	96
70		3x70 2XWY		2	1.56	32	26.88	0.785	3x70 2XWY	Copper XLPE Cables - Wire Armoured	3x70 2XWY	Copper	XLPE/EPR	70	0	3ph	0.08	260	Steel	133
95		3x95 2XWY		2	1.56	35	29.88	0.785	3x95 2XWY	Copper XLPE Cables - Wire Armoured	3x95 2XWY	Copper	XLPE/EPR	95	0	3ph	0.08	290	Steel	147
120		3x120 2XWY		2	1.72	39	33.56	0.785	3x120 2XWY	Copper XLPE Cables - Wire Armoured	3x120 2XWY	Copper	XLPE/EPR	120	0	3ph	0.08	290	Steel	165
150		3x150 2XWY		2	1.88	43	37.24	0.785	3x150 2XWY	Copper XLPE Cables - Wire Armoured	3x150 2XWY	Copper	XLPE/EPR	150	0	3ph	0.08	290	Steel	184
185		3x185 2XWY		2.5	2.04	48	41.42	0.785	3x185 2XWY	Copper XLPE Cables - Wire Armoured	3x185 2XWY	Copper	XLPE/EPR	185	0	3ph	0.08	290	Steel	255
240		3x240 2XWY		2.5	2.2	53	46.1	0.785	3x240 2XWY	Copper XLPE Cables - Wire Armoured	3x240 2XWY	Copper	XLPE/EPR	240	0	3ph	0.08	310	Steel	284
300		3x300 2XWY		2.5	2.36	58	50.78	0.785	3x300 2XWY	Copper XLPE Cables - Wire Armoured	3x300 2XWY	Copper	XLPE/EPR	300	0	3ph	0.08	330	Steel	313
25	16	3.5x25 2XWY		1.6	1.4	25	20.6	0.785	3.5x25 2XWY	Copper XLPE Cables - Wire Armoured	3.5x25 2XWY	Copper	XLPE/EPR	25	0.64	3ph	0.08	200	Steel	81
35	16	3.5x35 2XWY		1.6	1.4	27	22.6	0.785	3.5x35 2XWY	Copper XLPE Cables - Wire Armoured	3.5x35 2XWY	Copper	XLPE/EPR	35	0.457	3ph	0.08	230	Steel	89
50	25	3.5x50 2XWY		1.6	1.56	30	25.28	0.785	3.5x50 2XWY	Copper XLPE Cables - Wire Armoured	3.5x50 2XWY	Copper	XLPE/EPR	50	0.5	3ph	0.08	240	Steel	100
70	35	3.5x70 2XWY		2	1.56	35	29.88	0.785	3.5x70 2XWY	Copper XLPE Cables - Wire Armoured	3.5x70 2XWY	Copper	XLPE/EPR	70	0.5	3ph	0.08	260	Steel	147
95	50	3.5x95 2XWY		2	1.56	38	32.88	0.785	3.5x95 2XWY	Copper XLPE Cables - Wire Armoured	3.5x95 2XWY	Copper	XLPE/EPR	95	0.526	3ph	0.08	290	Steel	162
120	70	3.5x120 2XWY		2	1.72	42	36.56	0.785	3.5x120 2XWY	Copper XLPE Cables - Wire Armoured	3.5x120 2XWY	Copper	XLPE/EPR	120	0.583	3ph	0.08	290	Steel	180
150	70	3.5x150 2XWY		2	1.88	46	40.24	0.785	3.5x150 2XWY	Copper XLPE Cables - Wire Armoured	3.5x150 2XWY	Copper	XLPE/EPR	150	0.467	3ph	0.08	290	Steel	198
185	95	3.5x185 2XWY		2.5	2.04	51	44.42	0.785	3.5x185 2XWY	Copper XLPE Cables - Wire Armoured	3.5x185 2XWY	Copper	XLPE/EPR	185	0.514	3ph	0.08	290	Steel	274
240	120	3.5x240 2XWY		2.5	2.2	56	49.1	0.785	3.5x240 2XWY	Copper XLPE Cables - Wire Armoured	3.5x240 2XWY	Copper	XLPE/EPR	240	0.5	3ph	0.08	310	Steel	303
300	150	3.5x300 2XWY		2.5	2.36	60	52.78	0.785	3.5x300 2XWY	Copper XLPE Cables - Wire Armoured	3.5x300 2XWY	Copper	XLPE/EPR	300	0.5	3ph	0.08	330	Steel	325
1.5	1.5	4x1.5 2XWY		1.4	1.24	15	11.12	0.785	4x1.5 2XWY	Copper XLPE Cables - Wire Armoured	4x1.5 2XWY	Copper	XLPE/EPR	1.5	1	3ph	0.1	90	Steel	38
2.5	2.5	4x2.5 2XWY		1.4	1.24	16	12.12	0.785	4x2.5 2XWY	Copper XLPE Cables - Wire Armoured	4x2.5 2XWY	Copper	XLPE/EPR	2.5	1	3ph	0.1	90	Steel	42
4	4	4x4 2XWY		1.4	1.24	18	14.12	0.785	4x4 2XWY	Copper XLPE Cables - Wire Armoured	4x4 2XWY	Copper	XLPE/EPR	4	1	3ph	0.08	110	Steel	49
6	6	4x6 2XWY		1.4	1.24	21	17.12	0.785	4x6 2XWY	Copper XLPE Cables - Wire Armoured	4x6 2XWY	Copper	XLPE/EPR	6	1	3ph	0.08	130	Steel	59
10	10	4x10 2XWY		1.4	1.4	21	16.8	0.785	4x10 2XWY	Copper XLPE Cables - Wire Armoured	4x10 2XWY	Copper	XLPE/EPR	10	1	3ph	0.08	160	Steel	58
16	16	4x16 2XWY		1.6	1.4	22	17.6	0.785	4x16 2XWY	Copper XLPE Cables - Wire Armoured	4x16 2XWY	Copper	XLPE/EPR	16	1	3ph	0.08	180	Steel	69
25	25	4x25 2XWY		1.6	1.4	26	21.6	0.785	4x25 2XWY	Copper XLPE Cables - Wire Armoured	4x25 2XWY	Copper	XLPE/EPR	25	1	3ph	0.08	200	Steel	85
35	35	4x35 2XWY		1.6	1.4	28	23.6	0.785	4x35 2XWY	Copper XLPE Cables - Wire Armoured	4x35 2XWY	Copper	XLPE/EPR	35	1	3ph	0.08	230	Steel	93
50	50	4x50 2XWY		1.6	1.56	32	27.28	0.785	4x50 2XWY	Copper XLPE Cables - Wire Armoured	4x50 2XWY	Copper	XLPE/EPR	50	1	3ph	0.08	240	Steel	108
70	70	4x70 2XWY		2	1.56	37	31.88	0.785	4x70 2XWY	Copper XLPE Cables - Wire Armoured	4x70 2XWY	Copper	XLPE/EPR	70	1	3ph	0.08	260	Steel	157
95	95	4x95 2XWY		2	1.72	40	34.56	0.785	4x95 2XWY	Copper XLPE Cables - Wire Armoured	4x95 2XWY	Copper	XLPE/EPR	95	1	3ph	0.08	290	Steel	170
120	120	4x120 2XWY		2	1.88	44	38.24	0.785	4x120 2XWY	Copper XLPE Cables - Wire Armoured	4x120 2XWY	Copper	XLPE/EPR	120	1	3ph	0.08	290	Steel	189
150	150	4x150 2XWY		2.5	2.04	49	42.42	0.785	4x150 2XWY	Copper XLPE Cables - Wire Armoured	4x150 2XWY	Copper	XLPE/EPR	150	1	3ph	0.08	290	Steel	261
185	185	4x185 2XWY		2.5	2.2	54	47.1	0.785	4x185 2XWY	Copper XLPE Cables - Wire Armoured	4x185 2XWY	Copper	XLPE/EPR	185	1	3ph	0.08	290	Steel	290
240	240	4x240 2XWY		2.5	2.36	65	57.78	0.785	4x240 2XWY	Copper XLPE Cables - Wire Armoured	4x240 2XWY	Copper	XLPE/EPR	240	1	3ph	0.08	310	Steel	356
300	300	4x300 2XWY		3.15	2.52	68	59.81	0.785	4x300 2XWY	Copper XLPE Cables - Wire Armoured	4x300 2XWY	Copper	XLPE/EPR	300	1	3ph	0.08	330	Steel	464
25	25	2x25 2XFY		0.8	1.4	20	16.4	1	2x25 2XFY	Copper XLPE Cables - Flat Strip Armoured	2x25 2XFY	Copper	XLPE/EPR	25	1	1ph	0.08	200	Steel	41
35	35	2x35 2XFY		0.8	1.4	21	17.4	1	2x35 2XFY	Copper XLPE Cables - Flat Strip Armoured	2x35 2XFY	Copper	XLPE/EPR	35	1	1ph	0.08	230	Steel	44
50	50	2x50 2XFY		0.8	1.4	23	19.4	1	2x50 2XFY	Copper XLPE Cables - Flat Strip Armoured	2x50 2XFY	Copper	XLPE/EPR	50	1	1ph	0.08	240	Steel	49
70	70	2x70 2XFY		0.8	1.56	26	22.08	1	2x70 2XFY	Copper XLPE Cables - Flat Strip Armoured	2x70 2XFY	Copper	XLPE/EPR	70	1	1ph	0.08	260	Steel	55
95	95	2x95 2XFY		0.8	1.56	29	25.08	1	2x95 2XFY	Copper XLPE Cables - Flat Strip Armoured	2x95 2XFY	Copper	XLPE/EPR	95	1	1ph	0.08	290	Steel	63
120	120	2x120 2XFY		0.8	1.56	31	27.08	1	2x120 2XFY	Copper XLPE Cables - Flat Strip Armoured	2x120 2XFY	Copper	XLPE/EPR	120	1	1ph	0.08	290	Steel	68
150	150	2x150 2XFY		0.8	1.72	34	29.76	1	2x150 2XFY	Copper XLPE Cables - Flat Strip Armoured	2x150 2XFY	Copper	XLPE/EPR	150	1	1ph	0.08	290	Steel	75
185	185	2x185 2XFY		0.8	1.72	37	32.76	1	2x185 2XFY	Copper XLPE Cables - Flat Strip Armoured	2x185 2XFY	Copper	XLPE/EPR	185	1	1ph	0.08	290	Steel	82
240	240	2x240 2XFY		0.8	1.88	42	37.44	1	2x240 2XFY	Copper XLPE Cables - Flat Strip Armoured	2x240 2XFY	Copper	XLPE/EPR	240	1	1ph	0.08	310	Steel	94
300	300	2x300 2XFY		0.8	2.04	45	40.12	1	2x300 2XFY	Copper XLPE Cables - Flat Strip Armoured	2x300 2XFY	Copper	XLPE/EPR	300	1	1ph	0.08	330	Steel	101
16		3x16 2XFY		0.8	1.24	19	15.72	1	3x16 2XFY	Copper XLPE Cables - Flat Strip Armoured	3x16 2XFY	Copper	XLPE/EPR	16	0	3ph	0.08	180	Steel	39
25		3x25 2XFY		0.8	1.4	21	17.4	1	3x25 2XFY	Copper XLPE Cables - Flat Strip Armoured	3x25 2XFY	Copper	XLPE/EPR	25	0	3ph	0.08	200	Steel	44
35		3x35 2XFY		0.8	1.4	23	19.4	1	3x35 2XFY	Copper XLPE Cables - Flat Strip Armoured	3x35 2XFY	Copper	XLPE/EPR	35	0	3ph	0.08	230	Steel	49
50		3x50 2XFY		0.8	1.4	26	22.4	1	3x50 2XFY	Copper XLPE Cables - Flat Strip Armoured	3x50 2XFY	Copper	XLPE/EPR	50	0	3ph	0.08	240	Steel	56
70		3x70 2XFY		0.8	1.56	29	25.08	1	3x70 2XFY	Copper XLPE Cables - Flat Strip Armoured	3x70 2XFY	Copper	XLPE/EPR	70	0	3ph	0.08	260	Steel	63
95		3x95 2XFY		0.8	1.56	32	28.08	1	3x95 2XFY	Copper XLPE Cables - Flat Strip Armoured	3x95 2XFY	Copper	XLPE/EPR	95	0	3ph	0.08	290	Steel	71
120		3x120 2XFY		0.8	1.56	35	31.08	1	3x120 2XFY	Copper XLPE Cables - Flat Strip Armoured	3x120 2XFY	Copper	XLPE/EPR	120	0	3ph	0.08	290	Steel	78
150		3x150 2XFY		0.8	1.72	42	37.76	1	3x150 2XFY	Copper XLPE Cables - Flat Strip Armoured	3x150 2XFY	Copper	XLPE/EPR	150	0	3ph	0.08	290	Steel	95
185		3x185 2XFY		0.8	1.88	44	39.44	1	3x185 2XFY	Copper XLPE Cables - Flat Strip Armoured	3x185 2XFY	Copper	XLPE/EPR	185	0	3ph	0.08	290	Steel	99
240		3x240 2XFY		0.8	2.04	49	44.12	1	3x240 2XFY	Copper XLPE Cables - Flat Strip Armoured	3x240 2XFY	Copper	XLPE/EPR	240	0	3ph	0.08	310	Steel	111
300		3x300 2XFY		0.8	2.2	54	48.8	1	3x300 2XFY	Copper XLPE Cables - Flat Strip Armoured	3x300 2XFY	Copper	XLPE/EPR	300	0	3ph	0.08	330	Steel	123
25	16	3.5x25 2XFY		0.8	1.4	23	19.4	1	3.5x25 2XFY	Copper XLPE Cables - Flat Strip Armoured	3.5x25 2XFY	Copper	XLPE/EPR	25	0.64	3ph	0.08	200	Steel	49
35	16	3.5x35 2XFY		0.8	1.4	25	21.4	1	3.5x35 2XFY	Copper XLPE Cables - Flat Strip Armoured	3.5x35 2XFY	Copper	XLPE/EPR	35	0.457	3ph	0.08	230	Steel	54
50	25	3.5x50 2XFY		0.8	1.4	28	24.4	1	3.5x50 2XFY	Copper XLPE Cables - Flat Strip Armoured	3.5x50 2XFY	Copper	XLPE/EPR	50	0.5	3ph	0.08	240	Steel	61
70	35	3.5x70 2XFY		0.8	1.56	32	28.08	1	3.5x70 2XFY	Copper XLPE Cables - Flat Strip Armoured	3.5x70 2XFY	Copper	XLPE/EPR	70	0.5	3ph	0.08	260	Steel	71
95	50	3.5x95 2XFY		0.8	1.56	35	31.08	1	3.5x95 2XFY	Copper XLPE Cables - Flat Strip Armoured	3.5x95 2XFY	Copper	XLPE/EPR	95	0.526	3ph	0.08	290	Steel	78
120	70	3.5x120 2XFY		0.8	1.72	39	34.76	1	3.5x120 2XFY	Copper XLPE Cables - Flat Strip Armoured	3.5x120 2XFY	Copper	XLPE/EPR	120	0.583	3ph	0.08	290	Steel	87
150	70	3.5x150 2XFY		0.8	1.72	43	38.76	1	3.5x150 2XFY	Copper XLPE Cables - Flat Strip Armoured	3.5x150 2XFY	Copper	XLPE/EPR	150	0.467	3ph	0.08	290	Steel	97
185	95	3.5x185 2XFY		0.8	1.88	47	42.44	1	3.5x185 2XFY	Copper XLPE Cables - Flat Strip Armoured	3.5x185 2XFY	Copper	XLPE/EPR	185	0.514	3ph	0.08	290	Steel	107
240	120	3.5x240 2XFY		0.8	2.04	53	48.12	1	3.5x240 2XFY	Copper XLPE Cables - Flat Strip Armoured	3.5x240 2XFY	Copper	XLPE/EPR	240	0.5	3ph	0.08	310	Steel	121
300	150	3.5x300 2XFY		0.8	2.2	57	51.8	1	3.5x300 2XFY	Copper XLPE Cables - Flat Strip Armoured	3.5x300 2XFY	Copper	XLPE/EPR	300	0.5	3ph	0.08	330	Steel	130
16	16	4x16 2XFY		0.8	1.4	20	16.4	1	4x16 2XFY	Copper XLPE Cables - Flat Strip Armoured	4x16 2XFY	Copper	XLPE/EPR	16	1	3ph	0.08	180	Steel	41
25	25	4x25 2XFY		0.8	1.4	24	20.4	1	4x25 2XFY	Copper XLPE Cables - Flat Strip Armoured	4x25 2XFY	Copper	XLPE/EPR	25	1	3ph	0.08	200	Steel	51
35	35	4x35 2XFY		0.8	1.4	27	23.4	1	4x35 2XFY	Copper XLPE Cables - Flat Strip Armoured	4x35 2XFY	Copper	XLPE/EPR	35	1	3ph	0.08	230	Steel	59
50	50	4x50 2XFY		0.8	1.56	30	26.08	1	4x50 2XFY	Copper XLPE Cables - Flat Strip Armoured	4x50 2XFY	Copper	XLPE/EPR	50	1	3ph	0.08	240	Steel	66
70	70	4x70 2XFY		0.8	1.56	34	30.08	1	4x70 2XFY	Copper XLPE Cables - Flat Strip Armoured	4x70 2XFY	Copper	XLPE/EPR	70	1	3ph	0.08	260	Steel	76
95	95	4x95 2XFY		0.8	1.56	37	33.08	1	4x95 2XFY	Copper XLPE Cables - Flat Strip Armoured	4x95 2XFY	Copper	XLPE/EPR	95	1	3ph	0.08	290	Steel	83
120	120	4x120 2XFY		0.8	1.72	41	36.76	1	4x120 2XFY	Copper XLPE Cables - Flat Strip Armoured	4x120 2XFY	Copper	XLPE/EPR	120	1	3ph	0.08	290	Steel	92
150	150	4x150 2XFY		0.8	1.88	46	41.44	1	4x150 2XFY	Copper XLPE Cables - Flat Strip Armoured	4x150 2XFY	Copper	XLPE/EPR	150	1	3ph	0.08	290	Steel	104
185	185	4x185 2XFY		0.8	2.04	51	46.12	1	4x185 2XFY	Copper XLPE Cables - Flat Strip Armoured	4x185 2XFY	Copper	XLPE/EPR	185	1	3ph	0.08	290	Steel	116
240	240	4x240 2XFY		0.8	2.2	57	51.8	1	4x240 2XFY	Copper XLPE Cables - Flat Strip Armoured	4x240 2XFY	Copper	XLPE/EPR	240	1	3ph	0.08	310	Steel	130
300	300	4x300 2XFY		0.8	2.36	63	57.48	1	4x300 2XFY	Copper XLPE Cables - Flat Strip Armoured	4x300 2XFY	Copper	XLPE/EPR	300	1	3ph	0.08	330	Steel	144
6	6	2x6 A2XWY		1.4	1.24	19	15.12	0.785	2x6 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x6 A2XWY	Aluminium	XLPE/EPR	6	1	1ph	0.08	130	Steel	52
10	10	2x10 A2XWY		1.4	1.24	20	16.12	0.785	2x10 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x10 A2XWY	Aluminium	XLPE/EPR	10	1	1ph	0.08	160	Steel	56
16	16	2x16 A2XWY		1.4	1.4	19	14.8	0.785	2x16 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x16 A2XWY	Aluminium	XLPE/EPR	16	1	1ph	0.08	180	Steel	51
25	25	2x25 A2XWY		1.6	1.4	21	16.6	0.785	2x25 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x25 A2XWY	Aluminium	XLPE/EPR	25	1	1ph	0.08	200	Steel	65
35	35	2x35 A2XWY		1.6	1.4	23	18.6	0.785	2x35 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x35 A2XWY	Aluminium	XLPE/EPR	35	1	1ph	0.08	230	Steel	73
50	50	2x50 A2XWY		1.6	1.4	25	20.6	0.785	2x50 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x50 A2XWY	Aluminium	XLPE/EPR	50	1	1ph	0.08	240	Steel	81
70	70	2x70 A2XWY		1.6	1.56	28	23.28	0.785	2x70 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x70 A2XWY	Aluminium	XLPE/EPR	70	1	1ph	0.08	260	Steel	92
95	95	2x95 A2XWY		2	1.56	31	25.88	0.785	2x95 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x95 A2XWY	Aluminium	XLPE/EPR	95	1	1ph	0.08	290	Steel	128
120	120	2x120 A2XWY		2	1.56	34	28.88	0.785	2x120 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x120 A2XWY	Aluminium	XLPE/EPR	120	1	1ph	0.08	290	Steel	142
150	150	2x150 A2XWY		2	1.72	37	31.56	0.785	2x150 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x150 A2XWY	Aluminium	XLPE/EPR	150	1	1ph	0.08	290	Steel	156
185	185	2x185 A2XWY		2	1.88	40	34.24	0.785	2x185 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x185 A2XWY	Aluminium	XLPE/EPR	185	1	1ph	0.08	290	Steel	169
240	240	2x240 A2XWY		2.5	2.04	45	38.42	0.785	2x240 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x240 A2XWY	Aluminium	XLPE/EPR	240	1	1ph	0.08	310	Steel	237
300	300	2x300 A2XWY		2.5	2.2	49	42.1	0.785	2x300 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x300 A2XWY	Aluminium	XLPE/EPR	300	1	1ph	0.08	330	Steel	259
6		2x6 A2XWY		1.4	1.4	19	14.8	0.785	2x6 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x6 A2XWY	Aluminium	XLPE/EPR	6	0	3ph	0.08	130	Steel	51
10		2x10 A2XWY		1.4	1.4	21	16.8	0.785	2x10 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x10 A2XWY	Aluminium	XLPE/EPR	10	0	3ph	0.08	160	Steel	58
16		2x16 A2XWY		1.6	1.4	20	15.6	0.785	2x16 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x16 A2XWY	Aluminium	XLPE/EPR	16	0	3ph	0.08	180	Steel	62
25		2x25 A2XWY		1.6	1.4	23	18.6	0.785	2x25 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x25 A2XWY	Aluminium	XLPE/EPR	25	0	3ph	0.08	200	Steel	73
35		2x35 A2XWY		1.6	1.4	25	20.6	0.785	2x35 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x35 A2XWY	Aluminium	XLPE/EPR	35	0	3ph	0.08	230	Steel	81
50		2x50 A2XWY		1.6	1.56	29	24.28	0.785	2x50 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x50 A2XWY	Aluminium	XLPE/EPR	50	0	3ph	0.08	240	Steel	96
70		2x70 A2XWY		2	1.56	32	26.88	0.785	2x70 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x70 A2XWY	Aluminium	XLPE/EPR	70	0	3ph	0.08	260	Steel	133
95		2x95 A2XWY		2	1.56	35	29.88	0.785	2x95 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x95 A2XWY	Aluminium	XLPE/EPR	95	0	3ph	0.08	290	Steel	147
120		2x120 A2XWY		2	1.72	39	33.56	0.785	2x120 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x120 A2XWY	Aluminium	XLPE/EPR	120	0	3ph	0.08	290	Steel	165
150		2x150 A2XWY		2	1.88	43	37.24	0.785	2x150 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x150 A2XWY	Aluminium	XLPE/EPR	150	0	3ph	0.08	290	Steel	184
185		2x185 A2XWY		2.5	2.04	48	41.42	0.785	2x185 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x185 A2XWY	Aluminium	XLPE/EPR	185	0	3ph	0.08	290	Steel	255
240		2x240 A2XWY		2.5	2.2	53	46.1	0.785	2x240 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x240 A2XWY	Aluminium	XLPE/EPR	240	0	3ph	0.08	310	Steel	284
300		2x300 A2XWY		2.5	2.36	58	50.78	0.785	2x300 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x300 A2XWY	Aluminium	XLPE/EPR	300	0	3ph	0.08	330	Steel	313
25	16	2x25 A2XWY		1.6	1.4	25	20.6	0.785	2x25 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x25 A2XWY	Aluminium	XLPE/EPR	25	0.64	3ph	0.08	200	Steel	81
35	16	2x35 A2XWY		1.6	1.4	27	22.6	0.785	2x35 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x35 A2XWY	Aluminium	XLPE/EPR	35	0.457	3ph	0.08	230	Steel	89
50	25	2x50 A2XWY		1.6	1.56	30	25.28	0.785	2x50 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x50 A2XWY	Aluminium	XLPE/EPR	50	0.5	3ph	0.08	240	Steel	100
70	35	2x70 A2XWY		2	1.56	35	29.88	0.785	2x70 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x70 A2XWY	Aluminium	XLPE/EPR	70	0.5	3ph	0.08	260	Steel	147
95	50	2x95 A2XWY		2	1.56	38	32.88	0.785	2x95 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x95 A2XWY	Aluminium	XLPE/EPR	95	0.526	3ph	0.08	290	Steel	162
120	70	2x120 A2XWY		2	1.72	42	36.56	0.785	2x120 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x120 A2XWY	Aluminium	XLPE/EPR	120	0.583	3ph	0.08	290	Steel	180
150	70	2x150 A2XWY		2	1.88	46	40.24	0.785	2x150 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x150 A2XWY	Aluminium	XLPE/EPR	150	0.467	3ph	0.08	290	Steel	198
185	95	2x185 A2XWY		2.5	2.04	51	44.42	0.785	2x185 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x185 A2XWY	Aluminium	XLPE/EPR	185	0.514	3ph	0.08	290	Steel	274
240	120	2x240 A2XWY		2.5	2.2	56	49.1	0.785	2x240 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x240 A2XWY	Aluminium	XLPE/EPR	240	0.5	3ph	0.08	310	Steel	303
300	150	2x300 A2XWY		2.5	2.36	60	52.78	0.785	2x300 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x300 A2XWY	Aluminium	XLPE/EPR	300	0.5	3ph	0.08	330	Steel	325
6	6	2x6 A2XWY		1.4	1.24	21	17.12	0.785	2x6 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x6 A2XWY	Aluminium	XLPE/EPR	6	1	3ph	0.08	130	Steel	59
10	10	2x10 A2XWY		1.4	1.4	21	16.8	0.785	2x10 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x10 A2XWY	Aluminium	XLPE/EPR	10	1	3ph	0.08	160	Steel	58
16	16	2x16 A2XWY		1.6	1.4	22	17.6	0.785	2x16 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x16 A2XWY	Aluminium	XLPE/EPR	16	1	3ph	0.08	180	Steel	69
25	25	2x25 A2XWY		1.6	1.4	26	21.6	0.785	2x25 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x25 A2XWY	Aluminium	XLPE/EPR	25	1	3ph	0.08	200	Steel	85
35	35	2x35 A2XWY		1.6	1.4	28	23.6	0.785	2x35 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x35 A2XWY	Aluminium	XLPE/EPR	35	1	3ph	0.08	230	Steel	93
50	50	2x50 A2XWY		1.6	1.56	32	27.28	0.785	2x50 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x50 A2XWY	Aluminium	XLPE/EPR	50	1	3ph	0.08	240	Steel	108
70	70	2x70 A2XWY		2	1.56	37	31.88	0.785	2x70 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x70 A2XWY	Aluminium	XLPE/EPR	70	1	3ph	0.08	260	Steel	157
95	95	2x95 A2XWY		2	1.72	40	34.56	0.785	2x95 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x95 A2XWY	Aluminium	XLPE/EPR	95	1	3ph	0.08	290	Steel	170
120	120	2x120 A2XWY		2	1.88	44	38.24	0.785	2x120 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x120 A2XWY	Aluminium	XLPE/EPR	120	1	3ph	0.08	290	Steel	189
150	150	2x150 A2XWY		2.5	2.04	49	42.42	0.785	2x150 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x150 A2XWY	Aluminium	XLPE/EPR	150	1	3ph	0.08	290	Steel	261
185	185	2x185 A2XWY		2.5	2.2	54	47.1	0.785	2x185 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x185 A2XWY	Aluminium	XLPE/EPR	185	1	3ph	0.08	290	Steel	290
240	240	2x240 A2XWY		2.5	2.36	65	57.78	0.785	2x240 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x240 A2XWY	Aluminium	XLPE/EPR	240	1	3ph	0.08	310	Steel	356
300	300	2x300 A2XWY		3.15	2.52	68	59.81	0.785	2x300 A2XWY	Aluminium XLPE Cables - Wire Armoured	2x300 A2XWY	Aluminium	XLPE/EPR	300	1	3ph	0.08	330	Steel	464
25	25	2x25 A2XFY		0.8	1.4	20	16.4	1	2x25 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x25 A2XFY	Aluminium	XLPE/EPR	25	1	1ph	0.08	200	Steel	41
35	35	2x35 A2XFY		0.8	1.4	21	17.4	1	2x35 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x35 A2XFY	Aluminium	XLPE/EPR	35	1	1ph	0.08	230	Steel	44
50	50	2x50 A2XFY		0.8	1.4	23	19.4	1	2x50 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x50 A2XFY	Aluminium	XLPE/EPR	50	1	1ph	0.08	240	Steel	49
70	70	2x70 A2XFY		0.8	1.56	26	22.08	1	2x70 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x70 A2XFY	Aluminium	XLPE/EPR	70	1	1ph	0.08	260	Steel	55
95	95	2x95 A2XFY		0.8	1.56	29	25.08	1	2x95 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x95 A2XFY	Aluminium	XLPE/EPR	95	1	1ph	0.08	290	Steel	63
120	120	2x120 A2XFY		0.8	1.56	31	27.08	1	2x120 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x120 A2XFY	Aluminium	XLPE/EPR	120	1	1ph	0.08	290	Steel	68
150	150	2x150 A2XFY		0.8	1.72	34	29.76	1	2x150 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x150 A2XFY	Aluminium	XLPE/EPR	150	1	1ph	0.08	290	Steel	75
185	185	2x185 A2XFY		0.8	1.72	37	32.76	1	2x185 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x185 A2XFY	Aluminium	XLPE/EPR	185	1	1ph	0.08	290	Steel	82
240	240	2x240 A2XFY		0.8	1.88	42	37.44	1	2x240 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x240 A2XFY	Aluminium	XLPE/EPR	240	1	1ph	0.08	310	Steel	94
300	300	2x300 A2XFY		0.8	2.04	45	40.12	1	2x300 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x300 A2XFY	Aluminium	XLPE/EPR	300	1	1ph	0.08	330	Steel	101
16		2x16 A2XFY		0.8	1.24	19	15.72	1	2x16 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x16 A2XFY	Aluminium	XLPE/EPR	16	0	3ph	0.08	180	Steel	39
25		2x25 A2XFY		0.8	1.4	21	17.4	1	2x25 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x25 A2XFY	Aluminium	XLPE/EPR	25	0	3ph	0.08	200	Steel	44
35		2x35 A2XFY		0.8	1.4	23	19.4	1	2x35 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x35 A2XFY	Aluminium	XLPE/EPR	35	0	3ph	0.08	230	Steel	49
50		2x50 A2XFY		0.8	1.4	26	22.4	1	2x50 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x50 A2XFY	Aluminium	XLPE/EPR	50	0	3ph	0.08	240	Steel	56
70		2x70 A2XFY		0.8	1.56	29	25.08	1	2x70 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x70 A2XFY	Aluminium	XLPE/EPR	70	0	3ph	0.08	260	Steel	63
95		2x95 A2XFY		0.8	1.56	32	28.08	1	2x95 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x95 A2XFY	Aluminium	XLPE/EPR	95	0	3ph	0.08	290	Steel	71
120		2x120 A2XFY		0.8	1.56	35	31.08	1	2x120 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x120 A2XFY	Aluminium	XLPE/EPR	120	0	3ph	0.08	290	Steel	78
150		2x150 A2XFY		0.8	1.72	42	37.76	1	2x150 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x150 A2XFY	Aluminium	XLPE/EPR	150	0	3ph	0.08	290	Steel	95
185		2x185 A2XFY		0.8	1.88	44	39.44	1	2x185 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x185 A2XFY	Aluminium	XLPE/EPR	185	0	3ph	0.08	290	Steel	99
240		2x240 A2XFY		0.8	2.04	49	44.12	1	2x240 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x240 A2XFY	Aluminium	XLPE/EPR	240	0	3ph	0.08	310	Steel	111
300		2x300 A2XFY		0.8	2.2	54	48.8	1	2x300 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x300 A2XFY	Aluminium	XLPE/EPR	300	0	3ph	0.08	330	Steel	123
25	16	2x25 A2XFY		0.8	1.4	23	19.4	1	2x25 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x25 A2XFY	Aluminium	XLPE/EPR	25	0.64	3ph	0.08	200	Steel	49
35	16	2x35 A2XFY		0.8	1.4	25	21.4	1	2x35 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x35 A2XFY	Aluminium	XLPE/EPR	35	0.457	3ph	0.08	230	Steel	54
50	25	2x50 A2XFY		0.8	1.4	28	24.4	1	2x50 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x50 A2XFY	Aluminium	XLPE/EPR	50	0.5	3ph	0.08	240	Steel	61
70	35	2x70 A2XFY		0.8	1.56	32	28.08	1	2x70 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x70 A2XFY	Aluminium	XLPE/EPR	70	0.5	3ph	0.08	260	Steel	71
95	50	2x95 A2XFY		0.8	1.56	35	31.08	1	2x95 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x95 A2XFY	Aluminium	XLPE/EPR	95	0.526	3ph	0.08	290	Steel	78
120	70	2x120 A2XFY		0.8	1.72	39	34.76	1	2x120 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x120 A2XFY	Aluminium	XLPE/EPR	120	0.583	3ph	0.08	290	Steel	87
150	70	2x150 A2XFY		0.8	1.72	43	38.76	1	2x150 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x150 A2XFY	Aluminium	XLPE/EPR	150	0.467	3ph	0.08	290	Steel	97
185	95	2x185 A2XFY		0.8	1.88	47	42.44	1	2x185 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x185 A2XFY	Aluminium	XLPE/EPR	185	0.514	3ph	0.08	290	Steel	107
240	120	2x240 A2XFY		0.8	2.04	53	48.12	1	2x240 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x240 A2XFY	Aluminium	XLPE/EPR	240	0.5	3ph	0.08	310	Steel	121
300	150	2x300 A2XFY		0.8	2.2	57	51.8	1	2x300 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x300 A2XFY	Aluminium	XLPE/EPR	300	0.5	3ph	0.08	330	Steel	130
16	16	2x16 A2XFY		0.8	1.4	20	16.4	1	2x16 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x16 A2XFY	Aluminium	XLPE/EPR	16	1	3ph	0.08	180	Steel	41
25	25	2x25 A2XFY		0.8	1.4	24	20.4	1	2x25 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x25 A2XFY	Aluminium	XLPE/EPR	25	1	3ph	0.08	200	Steel	51
35	35	2x35 A2XFY		0.8	1.4	27	23.4	1	2x35 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x35 A2XFY	Aluminium	XLPE/EPR	35	1	3ph	0.08	230	Steel	59
50	50	2x50 A2XFY		0.8	1.56	30	26.08	1	2x50 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x50 A2XFY	Aluminium	XLPE/EPR	50	1	3ph	0.08	240	Steel	66
70	70	2x70 A2XFY		0.8	1.56	34	30.08	1	2x70 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x70 A2XFY	Aluminium	XLPE/EPR	70	1	3ph	0.08	260	Steel	76
95	95	2x95 A2XFY		0.8	1.56	37	33.08	1	2x95 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x95 A2XFY	Aluminium	XLPE/EPR	95	1	3ph	0.08	290	Steel	83
120	120	2x120 A2XFY		0.8	1.72	41	36.76	1	2x120 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x120 A2XFY	Aluminium	XLPE/EPR	120	1	3ph	0.08	290	Steel	92
150	150	2x150 A2XFY		0.8	1.88	46	41.44	1	2x150 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x150 A2XFY	Aluminium	XLPE/EPR	150	1	3ph	0.08	290	Steel	104
185	185	2x185 A2XFY		0.8	2.04	51	46.12	1	2x185 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x185 A2XFY	Aluminium	XLPE/EPR	185	1	3ph	0.08	290	Steel	116
240	240	2x240 A2XFY		0.8	2.2	57	51.8	1	2x240 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x240 A2XFY	Aluminium	XLPE/EPR	240	1	3ph	0.08	310	Steel	130
300	300	2x300 A2XFY		0.8	2.36	63	57.48	1	2x300 A2XFY	Aluminium XLPE Cables - Flat Strip Armoured	2x300 A2XFY	Aluminium	XLPE/EPR	300	1	3ph	0.08	330	Steel	144